## Slide 1: Designing and Manufacturing of 1KVA Single phase Tapped Shell type Transformer
Group Members
Kukil Saikia
Kukil Kashyap Borgohain
Aditya Raktim Baruah
Giri Raj Gogoi
Guide Name
Dr. Barnali Goswami

## Slide 2: Project Description
The undertaken project aims at designing a single phase 1kVA Transformer which has an automated 5% tap changer. The prime motive of this project is to explore the area of Machine Design with hands on experience which can further aid in research and development.

## Slide 3: Proposed Specification
Rating:- 1KVA
No load voltage ratio:- 230/120 volts
Frequency:- 50 Hz
Winding material:- Al
Maximum flux density:- 1.55 Tesla
Maximum current density:- 1.5 A/sq. mm

## Slide 4: Progress Overview
CORE DESIGN
YOKE DESIGN
WINDOW DESIGN
OVERALL FRAME DESIGN
WINDING DESIGN

## Slide 5: CORE DESIGN
Turns per volt : 2
Net iron area of core: 0.0726 sq. m
Gross iron area of core: 0.0807 sq. m
Height of outer limb: 0.2415 m
Depth of yoke: 0.1506 m

## Slide 6: YOKE DESIGN
Net yoke area: 0.0871 sq. m
Gross yoke area: 0.0968 sq. m
Yoke height: 0.4008 m

## Slide 7: WINDOW DESIGN
Window area: 1.6139 x 10 -4
Winding factor: 0.3307
Window width: 7.3343 x 10 -3
Window height: 0.220

## Slide 8: OVERALL FRAME DESIGN
Overall width of the frame: 0.9807 m
Overall height of the frame: 1.0216 m

## Slide 9: WINDING DESIGN
Primary Current: 4.35 A
Cross section area of Primary Winding: 2.905 sq. mm
Diameter of the wire: 1.92 ~ 2 mm
Number of turns in Primary: 460
Number of turns in Secondary: 240

## Slide 10: What’s next?
calculation of Losses
Efficiency
On load Tap Changer
Automated Cooling System
Cost Estimation

## Slide 11
Refferences:
1. Electrical Machine Design by AK Sawhney.
2. Design of Transformers by Indrajit Das Gupta.